## Buses
name | voltage_kv | zone | type
External_grid | 60 | External_grid | b
TEW_lv | 20 | RE_farm | b
TWT13_hv | 20 | RE_farm | n
TWT13_lv | 0.69 | RE_farm | n
SWG | 20 | RE_farm | b
TWT1_hv | 20 | RE_farm | n
TWT1_lv | 0.69 | RE_farm | n
TWT2_hv | 20 | RE_farm | n
TWT2_lv | 0.69 | RE_farm | n
TWT3_hv | 20 | RE_farm | n
TWT3_lv | 0.69 | RE_farm | n
TWT4_hv | 20 | RE_farm | n
TWT4_lv | 0.69 | RE_farm | n
TWT5_hv | 20 | RE_farm | n
TWT5_lv | 0.69 | RE_farm | n
TWT6_hv | 20 | RE_farm | n
TWT6_lv | 0.69 | RE_farm | n
TWT7_hv | 20 | RE_farm | n
TWT7_lv | 0.69 | RE_farm | n
TWT8_hv | 20 | RE_farm | n
TWT8_lv | 0.69 | RE_farm | n
TWT9_hv | 20 | RE_farm | n
TWT9_lv | 0.69 | RE_farm | n
TWT10_hv | 20 | RE_farm | n
TWT10_lv | 0.69 | RE_farm | n
TWT11_hv | 20 | RE_farm | n
TWT11_lv | 0.69 | RE_farm | n
TWT12_hv | 20 | RE_farm | n
TWT12_lv | 0.69 | RE_farm | n
TSP1_hv | 20 | RE_farm | n
TSP1_lv | 0.69 | RE_farm | n
TSP2_hv | 20 | RE_farm | n
TSP2_lv | 0.69 | RE_farm | n
TSP3_hv | 20 | RE_farm | n
TSP3_lv | 0.69 | RE_farm | n
TSP4_hv | 20 | RE_farm | n
TSP4_lv | 0.69 | RE_farm | n
TSP5_hv | 20 | RE_farm | n
TSP5_lv | 0.69 | RE_farm | n
TSP6_hv | 20 | RE_farm | n
TSP6_lv | 0.69 | RE_farm | n
TGLS1_lv | 10 | GreenLab_Skive | b
DAMP | 10 | GreenLab_Skive | b
QFUEL | 10 | GreenLab_Skive | b
NOMI | 10 | GreenLab_Skive | b
GLSBIO | 10 | GreenLab_Skive | b
EFUEL | 10 | GreenLab_Skive | b
REINTEG | 10 | GreenLab_Skive | b
TGLS2_lv | 10 | GreenLab_Skive | b
TB_hv | 10 | GreenLab_Skive | b
TB_lv | 0.4 | GreenLab_Skive | n
HYDRO | 10 | GreenLab_Skive | b
TSKCOL_lv | 10 | Skive_college | b
SKCOL | 10 | Skive_college | n

## Transformers
from | to | name | rating_mva | high_voltage_kv | low_voltage_kv | vk_% | vr_% | pfe_kw | i0_% | shift_deg
External_grid | TEW_lv | TEW | 80 | 60 | 20 | 11.4 | 0.25 | 50 | 0 | 0
TWT13_lv | TWT13_hv | TWT13 | 5 | 0.69 | 20 | 6.3 | 0.6 | 4.5 | 0 | 0
TWT1_lv | TWT1_hv | TWT1 | 5 | 0.69 | 20 | 6.3 | 0.6 | 4.5 | 0 | 0
TWT2_lv | TWT2_hv | TWT2 | 5 | 0.69 | 20 | 6.3 | 0.6 | 4.5 | 0 | 0
TWT3_lv | TWT3_hv | TWT3 | 5 | 0.69 | 20 | 6.3 | 0.6 | 4.5 | 0 | 0
TWT4_lv | TWT4_hv | TWT4 | 5 | 0.69 | 20 | 6.3 | 0.6 | 4.5 | 0 | 0
TWT5_lv | TWT5_hv | TWT5 | 5 | 0.69 | 20 | 6.3 | 0.6 | 4.5 | 0 | 0
TWT6_lv | TWT6_hv | TWT6 | 5 | 0.69 | 20 | 6.3 | 0.6 | 4.5 | 0 | 0
TWT7_lv | TWT7_hv | TWT7 | 5 | 0.69 | 20 | 6.3 | 0.6 | 4.5 | 0 | 0
TWT8_lv | TWT8_hv | TWT8 | 5 | 0.69 | 20 | 6.3 | 0.6 | 4.5 | 0 | 0
TWT9_lv | TWT9_hv | TWT9 | 5 | 0.69 | 20 | 6.3 | 0.6 | 4.5 | 0 | 0
TWT10_lv | TWT10_hv | TWT10 | 5 | 0.69 | 20 | 6.3 | 0.6 | 4.5 | 0 | 0
TWT11_lv | TWT11_hv | TWT11 | 5 | 0.69 | 20 | 6.3 | 0.6 | 4.5 | 0 | 0
TWT12_lv | TWT12_hv | TWT12 | 5 | 0.69 | 20 | 6.3 | 0.6 | 4.5 | 0 | 0
TSP1_lv | TSP1_hv | TSP1 | 5 | 0.69 | 20 | 6.3 | 0.6 | 4.5 | 0 | 0
TSP2_lv | TSP2_hv | TSP2 | 5 | 0.69 | 20 | 6.3 | 0.6 | 4.5 | 0 | 0
TSP3_lv | TSP3_hv | TSP3 | 5 | 0.69 | 20 | 6.3 | 0.6 | 4.5 | 0 | 0
TSP4_lv | TSP4_hv | TSP4 | 5 | 0.69 | 20 | 6.3 | 0.6 | 4.5 | 0 | 0
TSP5_lv | TSP5_hv | TSP5 | 5 | 0.69 | 20 | 6.3 | 0.6 | 4.5 | 0 | 0
TSP6_lv | TSP6_hv | TSP6 | 5 | 0.69 | 20 | 6.3 | 0.6 | 4.5 | 0 | 0
External_grid | TGLS1_lv | TGLS1 | 40 | 60 | 10 | 8.3 | 0.37 | 35 | 0 | 0
External_grid | TGLS2_lv | TGLS2 | 40 | 60 | 10 | 8.3 | 0.37 | 35 | 0 | 0
TB_hv | TB_lv | TB | 2 | 10 | 0.4 | 5.8 | 0.69 | 1.2 | 0 | 0
External_grid | TSKCOL_lv | TSKCOL | 2 | 60 | 10 | 5.8 | 0.69 | 1.2 | 0 | 0

## Cables
from | to | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | max_i_a | name | type | in_service | parallel | cross_section_mm2 | voltage_kv | material
TEW_lv | SWG | 4.64 | 0.0629 | 0.101 | 275 | 610 | CSWG | cs | 1 | 4 | 400 | 20 | AL
TWT13_hv | TEW_lv | 0.3 | 0.342 | 0.134 | 155 | 255 | CWT13 | cs | 1 | 1 | 70 | 20 | AL
TWT1_hv | SWG | 1.28 | 0.342 | 0.134 | 155 | 255 | CWT1 | cs | 1 | 1 | 70 | 20 | AL
TWT2_hv | SWG | 0.6 | 0.342 | 0.134 | 155 | 255 | CWT2 | cs | 1 | 1 | 70 | 20 | AL
TWT3_hv | SWG | 1.12 | 0.342 | 0.134 | 155 | 255 | CWT3 | cs | 1 | 1 | 70 | 20 | AL
TWT4_hv | SWG | 0.77 | 0.342 | 0.134 | 155 | 255 | CWT4 | cs | 1 | 1 | 70 | 20 | AL
TWT5_hv | SWG | 0.83 | 0.342 | 0.134 | 155 | 255 | CWT5 | cs | 1 | 1 | 70 | 20 | AL
TWT6_hv | SWG | 1.73 | 0.342 | 0.134 | 155 | 255 | CWT6 | cs | 1 | 1 | 70 | 20 | AL
TWT7_hv | SWG | 1.83 | 0.342 | 0.134 | 155 | 255 | CWT7 | cs | 1 | 1 | 70 | 20 | AL
TWT8_hv | SWG | 0.23 | 0.342 | 0.134 | 155 | 255 | CWT8 | cs | 1 | 1 | 70 | 20 | AL
TWT9_hv | SWG | 1.14 | 0.342 | 0.134 | 155 | 255 | CWT9 | cs | 1 | 1 | 70 | 20 | AL
TWT10_hv | SWG | 2.21 | 0.342 | 0.134 | 155 | 255 | CWT10 | cs | 1 | 1 | 70 | 20 | AL
TWT11_hv | SWG | 2.26 | 0.342 | 0.134 | 155 | 255 | CWT11 | cs | 1 | 1 | 70 | 20 | AL
TWT12_hv | SWG | 2.3 | 0.342 | 0.134 | 155 | 255 | CWT12 | cs | 1 | 1 | 70 | 20 | AL
TSP1_hv | SWG | 1 | 0.342 | 0.134 | 155 | 255 | CSP1 | cs | 1 | 1 | 70 | 20 | AL
TSP2_hv | SWG | 1.1 | 0.342 | 0.134 | 155 | 255 | CSP2 | cs | 1 | 1 | 70 | 20 | AL
TSP3_hv | SWG | 0.73 | 0.342 | 0.134 | 155 | 255 | CSP3 | cs | 1 | 1 | 70 | 20 | AL
TSP4_hv | SWG | 0.44 | 0.342 | 0.134 | 155 | 255 | CSP4 | cs | 1 | 1 | 70 | 20 | AL
TSP5_hv | SWG | 0.14 | 0.342 | 0.134 | 155 | 255 | CSP5 | cs | 1 | 1 | 70 | 20 | AL
TSP6_hv | SWG | 0.02 | 0.342 | 0.134 | 155 | 255 | CSP6 | cs | 1 | 1 | 70 | 20 | AL
TGLS1_lv | DAMP | 0.25 | 0.162 | 0.091 | 465 | 380 | CF1 | cs | 1 | 2 | 240 | 10 | AL
DAMP | QFUEL | 0.2 | 0.102 | 0.085 | 565 | 490 | CDtQ | cs | 1 | 2 | 400 | 10 | AL
QFUEL | NOMI | 0.3 | 0.102 | 0.085 | 565 | 490 | CQtN | cs | 1 | 1 | 400 | 10 | AL
NOMI | REINTEG | 0.45 | 0.162 | 0.091 | 465 | 380 | CNtR | cs | 0 | 1 | 240 | 10 | AL
TGLS1_lv | GLSBIO | 0.6 | 0.162 | 0.091 | 465 | 380 | CF2 | cs | 1 | 2 | 240 | 10 | AL
GLSBIO | EFUEL | 0.3 | 0.102 | 0.085 | 565 | 490 | CGtE | cs | 1 | 1 | 400 | 10 | AL
EFUEL | REINTEG | 0.05 | 0.162 | 0.091 | 465 | 380 | CEtR | cs | 1 | 1 | 240 | 10 | AL
TGLS2_lv | TB_hv | 0.05 | 0.102 | 0.085 | 565 | 490 | CF3 | cs | 1 | 2 | 400 | 10 | AL
TB_hv | HYDRO | 0.25 | 0.102 | 0.085 | 565 | 490 | CBtEl | cs | 1 | 2 | 400 | 10 | AL
TGLS2_lv | HYDRO | 0.3 | 0.102 | 0.085 | 565 | 490 | CF4 | cs | 0 | 2 | 400 | 10 | AL
TSKCOL_lv | SKCOL | 2 | 0.162 | 0.091 | 465 | 380 | CSKCOL | cs | 1 | 1 | 240 | 10 | AL

## Loads
bus | p_mw | q_mvar | name | in_service | cos_phi | sin_phi | s_mva | i_a
DAMP | 1 | 0.33427 | DAMP_l | 1 | 0.95 | 0.31756 | 1.0544 | 60.8753
QFUEL | 1.3 | 0.43456 | QFUEL_l | 1 | 0.95 | 0.31756 | 1.3707 | 79.1378
NOMI | 3.25 | 1.0864 | NOMI_l | 1 | 0.95 | 0.31756 | 3.4268 | 197.8446
GLSBIO | 3.25 | 1.0864 | GLSBIO_l | 1 | 0.95 | 0.31756 | 3.4268 | 197.8446
EFUEL | 0.3 | 0.10028 | EFUEL_l | 1 | 0.95 | 0.31756 | 0.31632 | 18.2626
REINTEG | 0.7 | 0.23399 | REINTEG_l | 1 | 0.95 | 0.31756 | 0.73807 | 42.6127
HYDRO | 14.5 | 4.847 | HYDRO_l | 1 | 0.95 | 0.31756 | 15.2887 | 882.6913
SKCOL | 2 | 0.66855 | SKCOL_l | 1 | 0.95 | 0.31756 | 2.1088 | 121.7505

## Storage
bus | p_mw | max_e_mwh | q_mvar | name | in_service
TB_lv | -1.6 | 1.6 | 0 | BESS_l | 1

## Generators
bus | p_mw | q_mvar | name | in_service
TWT13_lv | 4.2 | 0 | WT13 | 1
TWT1_lv | 4.2 | 0 | WT1 | 1
TWT2_lv | 4.2 | 0 | WT2 | 1
TWT3_lv | 4.2 | 0 | WT3 | 1
TWT4_lv | 4.2 | 0 | WT4 | 1
TWT5_lv | 4.2 | 0 | WT5 | 1
TWT6_lv | 4.2 | 0 | WT6 | 1
TWT7_lv | 4.2 | 0 | WT7 | 1
TWT8_lv | 4.2 | 0 | WT8 | 1
TWT9_lv | 4.2 | 0 | WT9 | 1
TWT10_lv | 4.2 | 0 | WT10 | 1
TWT11_lv | 4.2 | 0 | WT11 | 1
TWT12_lv | 4.2 | 0 | WT12 | 1
TSP1_lv | 4.47 | 0 | SP1 | 1
TSP2_lv | 4.47 | 0 | SP2 | 1
TSP3_lv | 4.47 | 0 | SP3 | 1
TSP4_lv | 4.47 | 0 | SP4 | 1
TSP5_lv | 4.47 | 0 | SP5 | 1
TSP6_lv | 4.47 | 0 | SP6 | 1